BILCO Type SVEV automatic smoke vents aid Firefighters in bringing a fire under control by removing smoke, heat and gasses from a burning building. Type SVEV single leaf smoke vents are designed with built-in louvers and a fixed safety guard to meet elevator-shaft code requirements. Available in galvanized steel or aluminum construction and customer sizes can be specified. For more information, please visit our website www.BILCO.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS FOR ELEVATOR SHAFTS

(BILCO TYPE SVev)

- GENERAL

      - SUMMARY

        - Work Included:  Provide factory-fabricated single-leaf automatic smoke vents.

      - SUBMITTALS

        - Product Data:  Submit manufacturer’s product data.

        - Shop Drawings: Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

        - Warranty:  Submit executed copy of manufacturer’s standard warranty.

      - QUALITY ASSURANCE

        - Manufacturer:  A minimum of 5 years experience manufacturing similar products.

        - Installer:  A minimum of 2 years experience installing similar products.

        - Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver products in manufacturer’s original packaging.  Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

      - WARRANTY

        - Manufacturer’s Warranty:  Provide manufacturer’s standard warranty. Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

- PRODUCTS

      - manufacturer

        - Basis-of-Design Manufacturer: Type SV Automatic Roof Smoke Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.BILCO.com.

      - AUTOMATIC ROOF FIRE VENT

        - Furnish and install where indicated on plans metal fire vent Type SVEV, size width: 36" (914mm) x length: 30" (762mm). Length denotes hinge side. The roof fire vent shall be single leaf and preassembled from the manufacturer.

        - Performance characteristics:

          - Vent(s) shall be UL listed. [In Canada only: Specify frame opening of 48” x 48” (195mm x 195mm) or greater for UL listing].

          - Cover shall be reinforced to support a minimum live load of 40 psf (195kg/m2) with a maximum deflection of 1/150th of the span or 90 psf (438kg/m2) wind uplift.

          - Lifting mechanism assemblies shall open the vent covers simultaneously when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

          - Entire roof fire vent shall be weather tight with fully welded corner joints on cover and curb.

          - Latch mechanisms shall hold the covers in the closed position without overstressing the fusible link and withstand 90 psf (438kg/m2) wind uplift forces acting on the cover.

          - Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent cover to open. The latch shall be designed for easy resetting, after a fire or test, so that the cover cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit.

        - Cover: Shall be [select: 14 gauge (1.9mm) galvannealed steel or 11 gauge (2.3mm) aluminum] with a 3” (76mm) beaded flange with formed reinforcing members. [For Type GSV substitute: Covers shall have a polycarbonate dome framed with rigid extruded aluminum and coated for UV resistance].

        - Cover insulation: Shall be fiberglass of 1” (25mm) thickness, fully covered and protected by a metal liner [select: 22 gauge (.8mm) galvannealed steel or 18 gauge (1mm) aluminum]. [Note: Omit cover insulation for Type GSV].

        - Curb: Shall be 12” (305mm) in height and of [select: 14 gauge (1.9mm) galvannealed steel or 11 gauge (2.3mm) aluminum]. Curb shall be formed with a 3-1/2” (89mm) flange with 7/16” (11mm) holes provided for securing to roof deck. Curb shall be equipped with integral metal capflashing of the same gauge and material as the curb and feature the Bil-Clip® flashing system, including stamped tabs, 6” (153mm) on center, to be bent inward to hold single-ply roofing membrane securely in place. Curb shall have a heavy extruded EPDM rubber gasket mechanically fastened to the top of the curb to assure a continuous seal when compressed by the cover.

        - Curb Fixed Safety Guard: A 3/4” (19mm) [select: #9 Steel or .125 (3.2mm) aluminum] raised expanded metal grid shall be welded to a fixed angle on all four sides inside the base of the curb.

        - Curb Louvers: 8” x 24” (203mm x 610mm) type T-63815 aluminum louvers shall be mounted into the three non-hinge sides of the curb. Louvers shall be supplied in a mill finish and be equipped with insect screens.

        - Curb insulation: Shall be rigid, high-density fiberboard of 1” (25mm) thickness on the outside of curb.

        - Lifting mechanisms: Manufacturer shall provide compression spring operators enclosed in telescopic tubes to open the covers against a snow/wind load. Upper tube shall be the outer tube to prevent accumulation of moisture, grit, and debris inside lower tube assembly. Lower tube shall interlock with a flanged support shoe.

        - Latch mechanism: Shall be the BILCO Thermolatch® positive hold/release mechanism controlled by a single UL listed 165°F (74°C) fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

        - Hardware

          - Heavy pintle hinges shall be provided.

          - Cover shall automatically lock in the open position with a rigid hold open arm equipped with a 1” (25mm) diameter red vinyl grip handle to permit easy release for closing.

          - All hardware shall be zinc plated and chromate sealed.

          - Cover hardware shall be bolted into heavy gauge channel reinforcing welded to the underside of the cover and concealed within the insulation space.

          - Heavy duty shock absorbers: Shall be provided to assure controlled opening of the covers.

        - Manual pull release cables: Interior and exterior cables with red vinyl grips shall be provided and allow the unit to be opened without disturbing the fusible link.

        - Finishes: Factory finish shall be [select: alkyd based red oxide primed steel or mill finish aluminum].

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

          - Test units for proper function and adjust until proper operation is achieved.

          - Test fusible link and install replacement fusible link after testing.

          - Repair finishes damaged during installation.

          - Restore finishes so no evidence remains of corrective work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION