BILCO Type DSH double leaf automatic smoke vents aid Firefighters in bringing a fire under control by removing smoke, heat and gasses from a burning building. Type DSH double leaf smoke vents are the most economical way to add fire venting protect in large areas such as warehouses or manufacturing facilities. Available in galvanized steel or aluminum construction and in a number of standard sizes. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS

(BILCO TYPE DSH)

- GENERAL

      - SUMMARY

        - Work Included:  Provide factory-fabricated double-leaf automatic smoke vents.

      - SUBMITTALS

        - Product Data:  Submit manufacturer’s product data.

        - Shop Drawings: Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

        - Warranty:  Submit executed copy of manufacturer’s standard warranty.

      - QUALITY ASSURANCE

        - Manufacturer:  A minimum of 5 years experience manufacturing similar products.

        - Installer:  A minimum of 2 years experience installing similar products.

        - Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver products in manufacturer’s original packaging.  Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

      - WARRANTY

        - Manufacturer’s Warranty: Provide manufacturer’s standard warranty. Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

- PRODUCTS

      - manufacturer

        - Basis-of-Design Manufacturer: Type DSH Automatic Roof Smoke Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

      - AUTOMATIC ROOF FIRE VENT

        - Furnish and install where indicated on plans metal fire vent Type DSH, size [insert: width (______) x length (______)]. Length denotes hinge side. The roof fire vent shall be double leaf and preassembled from the manufacturer.

        - Performance characteristics:

          - Vent shall be UL listed. Comply with UL 793 and UL 790 Class A (burning brand test).

          - Operation: Vent covers shall open simultaneously against a 10 psf (49kg/m2) snow/wind load when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

          - Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent cover to open. The latch shall be designed for easy resetting, after a fire or test, so that the cover cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit. Latch mechanism shall hold the covers in the closed position without overstressing the fusible link and withstand 90 psf (438kg/m2) wind uplift forces acting on the covers.

          - Covers shall be reinforced to support a minimum live load of 40 psf (195kg/m2) with a maximum deflection of 1/150th of the span or 20 psf (97kg/m2) wind uplift.

          - Entire roof fire vent shall be weather tight with fully welded corner joints on cover and curb.

        - Covers: Shall be [select: 14 gauge (1.9mm) paint bond G-90 galvanized steel or 11 gauge (2.3mm) aluminum] with a 3” (76mm) beaded flange with formed reinforcing members.

        - Cover insulation: Shall be fiberglass of 1” (25mm) thickness, fully covered and protected by a metal liner [select: 22 gauge (.8mm) paint bond G-90 galvanized steel or 18 gauge (1mm) aluminum].

        - Curb: Shall be 12” (305mm) in height and of [select: 14 gauge (1.9mm) paint bond G-90 galvanized steel or 11 gauge (2.3mm) aluminum]. Curb shall be formed with a 3-1/2” (89mm) flange with 7/16” (11mm) holes provided for securing to roof deck. Curb shall be equipped with integral metal capflashing of the same gauge and material as the curb and feature the Bil-Clip® flashing system, including stamped tabs, 6” (153mm) on center, to be bent inward to hold single-ply roofing membrane securely in place. Curb shall have a heavy extruded EPDM rubber gasket that is mechanically fastened to the top of the curb to assure a continuous seal when compressed by the covers.

        - Curb insulation: Shall be rigid, high-density fiberboard of 1” (25mm) thickness on the outside of curb.

        - Lifting mechanisms: Manufacturer shall provide high performance gas spring operators to open the covers against a snow/wind load. Gas springs shall automatically lock covers in the fully open position. A release mechanism shall be provided to allow covers to be closed. Gas springs shall have integral dampers to assure a controlled rate of cover opening and have a cyclic durability of 50,000 cycles.

        - Latch mechanism: Shall be the BILCO Thermolatch®II positive hold/release mechanism with a separate latching point for each cover controlled by a single UL listed 165°F (74°C) fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

        - Hardware

          - Heavy pintle hinges shall be provided.

          - Gas springs have a powder coated outer tube and chromate plated inner rod. All other hardware is zinc plated/chromate sealed or galvanized steel.

          - Cover hardware shall be bolted into heavy gauge channel reinforcing welded to the underside of the cover and concealed within the insulation space.

        - Manual pull release cables: Interior and exterior cables with red vinyl grips shall be provided and allow the unit to be opened without disturbing the fusible link.

        - Finishes: Factory finish shall be [select: alkyd based red oxide primed steel or mill finish aluminum].

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

          - Test units for proper function and adjust until proper operation is achieved.

          - Test fusible link and install replacement fusible link after testing.

          - Repair finishes damaged during installation.

          - Restore finishes so no evidence remains of corrective work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION