BILCO Type LV automatic smoke vents provide the security a smoke vent with the added benefits of a skylight. The Lumivent® features a multi-wall polycarbonate cover design that resists UV degradation and offers superior insulation performance over traditional domes. Vents are available in aluminum construction and in a number of UL-Listed standard sizes. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS

(BILCO TYPE LV)

- GENERAL

      - SUMMARY

        - Work Included:  Provide factory-fabricated double-leaf automatic smoke vents.

      - SUBMITTALS

        - Product Data:  Submit manufacturer’s product data.

        - Shop Drawings: Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

        - Warranty:  Submit executed copy of manufacturer’s standard warranty.

      - QUALITY ASSURANCE

        - Manufacturer:  A minimum of 5 years experience manufacturing similar products.

        - Installer:  A minimum of 2 years experience installing similar products.

        - Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver products in manufacturer’s original packaging. Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

      - WARRANTY

        - Manufacturer’s Warranty:  Provide manufacturer’s standard warranty.  Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

- PRODUCTS

      - manufacturer

        - Basis-of-Design Manufacturer:  Type LV Lumivent, Translucent Automatic Roof Fire Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

      - AUTOMATIC ROOF FIRE VENT

        - Furnish and install where indicated on plans metal fire vent Type LV, size [insert: width (______) x length (______)]. Length denotes hinge side. The roof fire vent shall be double leaf. The roof fire vent shall be preassembled from the manufacturer.

        - Performance characteristics:

          - Vent(s) shall be UL listed.

          - Covers shall be reinforced to support a minimum live load of 40 psf (195kg/m2) with a maximum deflection of 1/150th of the span.

          - Lifting mechanism assemblies shall open the vent covers simultaneously when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

          - Entire roof fire vent shall be weather tight.

          - Latch mechanisms shall hold the covers in the closed position without overstressing the fusible link and withstand 40 psf (195kg/m2) wind uplift forces acting on the cover.

          - Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent covers to open. The latch shall be designed for easy resetting, after a fire or test, so that the covers cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit.

        - Covers: Shall be constructed with a translucent multi-wall polycarbonate sheet framed with rigid extruded aluminum and coated for UV resistance.  Glazing shall provide an R-factor of 2.38 (U=2.39W/m2K) per ASTMD236.  Covers shall slope 4:12 per Section 2610.3 of IBC (ICC).

        - Curb: Shall be 12" (305mm) in height and of 11 gauge (2.3mm) aluminum, pitched 20° to a fixed center channel. Curb shall be formed with a 3-1/2" (89mm) flange with 7/16" (11mm) holes provided for securing to roof deck. Curb shall be equipped with an integral 11 gauge (2.3mm) aluminum capflashing and feature the Bil-Clip® flashing system, including stamped tabs, 6" (153mm) on center, to be bent inward to hold single-ply roofing membrane securely in place.  Curb shall have a dual-durometer co-extruded EPDM rubber gasket that is mechanically fastened to the top of the curb to assure a continuous seal when compressed against the underside of the cover.

        - Curb insulation: Shall be rigid, high-density fiberboard of 1" (25mm) thickness on the outside of curb.

        - Lifting mechanisms: Manufacturer shall provide high performance gas springs which apply forces to the center of the cover and open the covers in a controlled manner against 10 lb/ft2 (49Kg/m2)] snow/wind load. Gas springs shall have a cyclic durability of 50,000 cycles and have a corrosion resistant outer tube and inner rod.

        - Latch mechanism: Shall be the BILCO Thermolatch® II positive hold/release mechanism with a separate latching point for each cover controlled by a single UL listed 165°F (74°C) fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

        - Hardware

          - Heavy duty Type 316 stainless steel pintle hinges.

          - Covers shall automatically lock in the open position with a rigid hold open arm equipped with a 1" (25mm) diameter red vinyl grip handle to permit easy release for closing.

          - All hardware (unless specified otherwise) shall be zinc plated and chromate sealed. Cover hardware shall be bolted into heavy gauge channel reinforcing welded to the underside of the cover.

        - Manual pull release cables: Interior and exterior cables with red vinyl grips shall be provided and allow the unit to be opened without disturbing the fusible link.

        - Finishes: Factory finish shall be mill finish aluminum.

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

          - Test units for proper function and adjust until proper operation is achieved.

          - Test fusible link and install replacement fusible link after testing.

          - Repair finishes damaged during installation.

          - Restore finishes so no evidence remains of corrective work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION